## Sheet1
Description | Register | Units | Size (INT16) | Data Type | Access
Current A | 50000 | A | 2 | FLOAT32 | R
Current B | 50002 | A | 2 | FLOAT32 | R
Current C | 50004 | A | 2 | FLOAT32 | R
Current N | 50006 | A | 2 | FLOAT32 | R
Current Avg | 50008 | A | 2 | FLOAT32 | R
Current Unbalance A | 50010 | % | 2 | FLOAT32 | R
Current Unbalance B | 50012 | % | 2 | FLOAT32 | R
Current Unbalance C | 50014 | % | 2 | FLOAT32 | R
Voltage A-B | 50016 | V | 2 | FLOAT32 | R
Voltage B-C | 50018 | V | 2 | FLOAT32 | R
Voltage C-A | 50020 | V | 2 | FLOAT32 | R
Voltage A-N | 50022 | V | 2 | FLOAT32 | R
Voltage B-N | 50024 | V | 2 | FLOAT32 | R
Voltage C-N | 50026 | V | 2 | FLOAT32 | R
Voltage L-L Avg | 50028 | V | 2 | FLOAT32 | R
Voltage L-N Avg | 50030 | V | 2 | FLOAT32 | R
Active Power A | 50032 | kW | 2 | FLOAT32 | R
Active Power B | 50034 | kW | 2 | FLOAT32 | R
Active Power C | 50036 | kW | 2 | FLOAT32 | R
Active Power Total | 50038 | kW | 2 | FLOAT32 | R
Reactive Power A | 50040 | kVAR | 2 | FLOAT32 | R
Reactive Power B | 50042 | kVAR | 2 | FLOAT32 | R
Reactive Power C | 50044 | kVAR | 2 | FLOAT32 | R
Reactive Power Total | 50046 | kVAR | 2 | FLOAT32 | R
Power Factor A | 50048 | --- | 2 | 4Q FP PF | R
Power Factor B | 50050 | --- | 2 | 4Q FP PF | R
Power Factor C | 50052 | --- | 2 | 4Q FP PF | R
Power Factor Total | 50054 | --- | 2 | 4Q FP PF | R
Active Energy Delivered Phase A | 50056 | Wh | 4 | INT64 | R
Active Energy Delivered Phase B | 50060 | Wh | 4 | INT64 | R
Active Energy Delivered Phase C | 50064 | Wh | 4 | INT64 | R
Active Energy Delivered (Into Load) | 50068 | Wh | 4 | INT64 | R
Reactive Energy Delivered Phase A | 50072 | VARh | 4 | INT64 | R
Reactive Energy Delivered Phase B | 50076 | VARh | 4 | INT64 | R
Reactive Energy Delivered Phase C | 50080 | VARh | 4 | INT64 | R
Reactive Energy Delivered | 50084 | VARh | 4 | INT64 | R
Active Power Dmd Phase A | 50088 | --- | 2 | FLOAT32 | R
Active Power Dmd Phase B | 50090 | --- | 2 | FLOAT32 | R
Active Power Dmd Phase C | 50092 | --- | 2 | FLOAT32 | R
Active Power Dmd Total | 50094 | --- | 2 | FLOAT32 | R
Alarm flags phase A/AB | 50096 | --- | 1 | Bitmap | R
Alarm flags phase B/BC | 50097 | --- | 1 | Bitmap | R
Alarm flags phase C/CA | 50098 | --- | 1 | Bitmap | R